Oceanside Fire Requirements

Community Development Department

Planning Division

TO:	Project Planning

FROM:	Tim Rise

Plans Examiner

DATE:	February 24, 2021

SUBJECT:	El Corazon Mixed Use

3302 Senior Center Dr

D19-00018

Fire Department Conditions of Approval

1. Fire access roadways must be marked "No Parking" per Oceanside Fire requirements.

2. Gates proposed for both entrances must comply with Oceanside Fire Master Plan requirements.

3. Knox key override and Opticom strobe activated devices required for gates.

4. Provide Knox key box at pool gate and entrance to recreation center.

5. System type to be determined by occupancy classification and California Building Code Chapter 5.

6. Show locations of fire sprinkler system fire department connections and system control valves for NFPA 13 and/or 13R systems.

7. Provide minimum six inches high building address numbers on buildings.  Numbers must be visible from roadway on which the building is addressed.

8. Fire alarm system may be required for residential buildings.

9. Street elevation changes at entrances may not exceed fire vehicle angle of approach and departure

10. Plans for private underground fire lines must be submitted to the fire department for review under separate permit.  Fire lines must comply with Oceanside Fire standard.

11. All required emergency egress openings in sleeping rooms below four stories must be accessible by fire department ground ladders.

12. Provide Fire Master Plan per Oceanside standard.

13. Provide lighted address marquee at main entrance to the project. This location must be approved by the Oceanside Fire Department.