Oceanside Fire Requirements

Community Development Department

Planning Division

TO:	Project Planning

FROM:	Tim Rise

Plans Examiner

DATE:	March 22, 2021

SUBJECT:	4002 Vista Way

One story 16-bed Psychiatric Hospital Facility

D21-00004

Fire Department Comments:

- Hydrants required within 400’ of all exterior walls of the structure.

- Note if hydrants will be public or private. If private, a looped system is required.

3.   Fire sprinklers required per 2016 NFPA 13 standards.

3.   Fire sprinklers must have a dedicated fire line to the building.

4.   Fire alarm system required per 2016 NFPA 72.

5.   Dedicated FACP room in main lobby required.

6.   Dedicated fire riser room.

7.   Driveway off of Waring Rd. must not exceed 12% grade.

8.   Bottom of driveway must not exceed 8 degrees for approach and departures.

9.   Hose pull distance must be within 150’ of all exterior walls of the structure. This is measured from an approved fire access roadway on an approved route around the building and not as the crow flies.

10.  Show gate details. Gates must be provided with proper signage for fire department access.

11. Gates must be provided with Opti-com for emergency access.

12. Knox key switches required on all vehicle access gates. Gates that are manually operated must have Knox Padlocks.

13. Knox box required at main entrance.

14. Fire department hammerhead must meet our minimum standards per our Fire Master Plan.

15. Fire Department Site Plan must be submitted to the fire department for review.

16. A minimum of 5 feet required around the structure for emergency access.

17. Smoke and carbon monoxide detectors are required per 2019 California Fire Code.

18. Prior to delivery of combustible materials or start of combustible construction, the approved, permanent water supply (fire hydrants) must be installed, tested and placed in service prior to delivery of combustible materials or start of combustible construction.

19. Fire extinguishers are required and shall be included on the plans submitted for plan check.

20. Addresses must be clearly visible and legible from Vista Way. Project may need an address board at main entrance.

21. The building must support adequate radio coverage operating on the 800MHz Countywide Communication System. When tested, if the 800MHz signal strength readings (RSSI) fall below 65 in any portion of the building, either above or below grade as measured by an 800 MHz portable radio, the purchase and installation of one or more bidirectional amplifier radio coverage enhancers is required.

22. Pre-Con meeting required prior to combustible materials dropped on site.

23. Knox box required at main entrance.

24. Fire lane stripping and signage must comply with the Oceanside Fire Department Master Plan.