Water Utilities Project Comments & Conditions

Date:	September 30th, 2019

Planner:	Sergio Madera

From: 	Ibrahim Hassan

RE: 	T19-00004 OCEAN KAMP

Submittal 1

STATUS: REVISE AND RESUBMIT

The following comment(s) will need to be addressed to deem the application complete.

- Define zones R-1 through R-6 listed on A1.1.

- A water & sewer studies must be prepared by the developer, at the developer’s expense, and reviewed and approved by the Water Utilities Department. Each analysis shall consider all proposed and future development on the site (include zones R1-R6), as well as provided projected sewer flow rates and tie in locations.

- Show Public water main with minimum 20’easement in private road along northern portion of Development.

- The single feed loop shown on plans is not acceptable. The on-site fire system shall be private and looped with two connections to the City’s water system.  Show Public water main with minimum 20’easement in private road along northern portion of Development. One connection shall be off the existing steel main in Foussat Road and second off the existing main in Mission Ave; each having a backflow assembly. The existing 4” AC main can be used to feed loop, but shall be upsized to meet City’s standard and Water study requirements.

- Relocate all utilities in Foussat Street (old Foussat) to Foussat Road. Existing 8” Forcemain (Marlado) shall be relocated into Foussat Road, and run along southern portion of development with a dedicated utility easement & access road into the existing 8” PVC lateral on property.

- All Onsite private sewer shall Discharge into existing 8” PVC Lateral. Revise Civil plans

- Show on plan, each commercial building with a separate City water meter. Design plans will show a private sub-meter for each commercial suite where there is more than one unit within a building. Water supply lines after the City meters to each building shall be privately maintained and have a backflow assembly.

- Show on plan, dedicated City water meter(s) for hotel resort and associated buildings. Design plans will show a private sub-meter for buildings maintained by hotel resort. Water supply lines after the City meters to each building shall be privately maintained and have a backflow assembly.

- Show on plan, a separate City water meter for pools maintained by resort hotel, such as wave pool, lazy river, adult pool, children’s splash, etc.

- Maximum fire hydrant spacing is 300 feet and all portions of commercial or industrial buildings shall be within 150 feet of an approved fire hydrant accessible to the fire department vehicles per Section 2.6 of the Water, Sewer, and Recycled Water Design and Construction Manual.

- A block wall enclosure with double swing gates shall be provided around the existing air-release valves for containment during cleaning and maintenance operations.  This enclosure shall provide access for required maintenance vehicles at all times.

- Beach sand Is proposed throughout portions of development. Oil and Sand Interceptor(s) shall be installed, as described by the latest adopted California Plumbing Code Chapter 10, relating to garages, gasoline stations, wash racks or when deemed necessary. Interceptor shall be maintained in accordance with the Fats, Oil, and Grease permit. The location shall be shown on the approved Engineering Plans with reference to Building Plans for design and detail.

- A Grease Interceptor, as required per City of Oceanside Ordinance 07-OR0021-1 & 18-OR0021-1 relating to food service establishments shall be on each building sewer when deemed necessary in an appropriate outside location and shall be maintained by the property owner. The grease interceptor shall be shown on Engineering Plans with reference to Building Plans for design and detail.

General conditions:

- For developments requiring new water service or increased water service to a property, the landowner must enter into an agreement with the City providing for landowner’s assignment of any rights to divert or extract local groundwater supplies for the benefit of the property to receive new or increased water service, in return for water service from the City, upon such terms as may be provided by the Water Utilities Director.

- All existing active and non-active groundwater wells must be shown on conceptual, grading, and improvement plans.

- The developer will be responsible for developing all water and sewer utilities necessary to develop the property. Any relocation of water and/or sewer utilities is the responsibility of the developer and shall be done by an approved licensed contractor at the developer’s expense.

- All Water and Wastewater construction shall conform to the most recent edition of the Water, Sewer, and Recycled Water Design and Construction Manual or as approved by the Water Utilities Director.

- The property owner shall maintain private water and wastewater utilities located on private property.

- Water services and sewer laterals constructed in existing right-of-way locations are to be constructed by an approved and licensed contractor at developer’s expense.

- Provide a separate irrigation water meter with reduced pressure principle backflow device for common area landscaping. Meter shall be managed and paid for by the Homeowner’s Association for the development. Irrigation meter may be a dedicated water meter, or a private sub-meter.

- Per the latest approved California Fire Code, all new residential units shall be equipped with fire sprinkler system.

- Buildings requiring an NFPA 13 or NFPA 13R automatic sprinkler system for fire protection shall have a dedicated fire service connection to a public water main with a double check detector backflow assembly. Location of the backflow assembly must be approved by Fire Department.

The following conditions shall be met prior to the approval of engineering design plans.

- All public water and/or sewer facilities not located within the public right-of-way shall be provided with easements sized according to the Water, Sewer, and Recycled Water Design and Construction Manual.  Easements shall be constructed for all weather access.

- Any water and/or sewer improvements required to develop the proposed property will need to be included in the improvement plans and designed in accordance with the Water, Sewer, and Recycled Water Design and Construction Manual.

- No trees, structures or building overhang shall be located within any water or wastewater utility easement.

- All lots with a finish pad elevation located below the elevation of the next upstream manhole cover of the public sewer shall be protected from backflow of sewage by installing and maintaining an approved type backwater valve, per the latest adopted California Plumbing Code.

- The developer shall construct a public recycled water system that will serve each lot and or parcels that are located in the proposed project in accordance with the City of Oceanside Ordinance No. 14-OR0565-1.  The proposed recycled water system shall be located in the public right-of-way or in a public utility easement.

- Recycled water is anticipated to be supplied through the Fallbrook outfall line in the near future. When recycled water becomes available, this property shall be required to convert its irrigation supply to recycled water. The irrigation system shall be designed in anticipation of a future recycled water service and meter.

- An inspection manhole <for industrial and commercial waste> as described by the Water, Sewer, and Recycled Water Design and Construction Manual, shall be on each building sewer lateral and the location shall be called out on the approved engineering plans.

- Connections to public sewer main with 6-inch or larger sewer lateral will require a new sewer manhole for connection to main per Section 3.3 of Water, Sewer, and Recycled Water Design and Construction Manual.

- A separate irrigation meter and connection with an approved backflow prevention device is required to serve common landscaped areas and shall be displayed on the plans.

- Provide peak irrigation flows per zone or control valve to verify size of irrigation meter and reduced pressure principle backflow device on Landscape Plans.

- All existing and proposed sewer manholes on site shall show on plans an access road, turf block, or pavement that can support H-20 loading for sewer vactor truck. Access road or pavement must have a minimum turning radius of 46-feet (outer wheel) for curb clearance and a wall clearance of 46’-11”. Truck length is 41’-6”.

- Provide stationing and offsets for existing and proposed water service connections and sewer laterals on plans.

- Where private sewer system is shared with other tenants, a Property Management Company and CC&Rs should address the maintenance, repair, and replacement of “shared” sewer lateral or facilities.

- Any unused water services or sewer laterals by the proposed development or redevelopment, shall be abandoned in accordance with Water Utilities requirements.

The following conditions of approval shall be met prior to building permit issuance.

- Show location and size of existing and proposed water meter(s) on site plan of building plans. Show waterline from proposed meter to connection point to building or residence.

- Show location and size of existing and proposed sewer lateral(s) from property line or connection to sewer main to connection point at building or residence.

- Provide table of fixture count and flow calculations per the latest adopted California Plumbing Code to size water meter and service lines on site plan of building plans.

- If a larger water meter is required, then the incremental increase in water and sewer buy-in fees between the existing and proposed meter size will be charged. If the existing water service connection is less than the proposed meter size, then the Owner/Developer will be required to abandon the existing water service and show on engineering and building plans the location and size of the new service connection to public main.

- Provide drainage fixture unit count per the latest adopted California Plumbing Code to size sewer lateral for property.

- If a Grease Interceptor is required per City of Oceanside Ordinance 07-OR0021-1, then building plans must show sizing calculations per the latest California Plumbing Code, the location, the make and model, and plumbing schematic showing the required appurtenances at each building sewer lateral.

- If a Sand and Oil Separator is required, then building plans must show drainage fixture unit count and calculations per the latest California Plumbing Code to size oil and sand separator and show on plans the location, make and model of separator, inlet/outlet piping, and a plumbing schematic of the separator along with the required appurtenances at each building sewer lateral.

- Water and Wastewater Buy-in fees and the San Diego County Water Authority Fees are to be paid to the City at the time of Building Permit issuance per City Code Section 32B.7.