Water Utilities Project Comments & Conditions
Date:	June 22, 2022		
Planner:	Patricia Anders
From: 	Bryan Kallenbaugh
RE:	APN-165-493-47: 12 1-Story Detached Units, & 2 1-Story Triplex Units		Submittal #3: T21-00002, D21-00005, CUP21-00005
STATUS: APPROVED WITH THE FOLLOWING CONDITIONS 
General Conditions:
1. The developer will be responsible for developing all water and sewer utilities necessary to develop the property. Any relocation of water and/or sewer utilities is the responsibility of the developer and shall be done by an approved licensed contractor at the developer’s expense.
2. All Water and Wastewater construction shall conform to the most recent edition of the Water, Sewer, and Recycled Water Design and Construction Manual or as approved by the Water Utilities Director.
3. The property owner shall maintain private water and wastewater utilities located on private property.
4. Water services and sewer laterals constructed in existing right-of-way locations are to be constructed by an approved and licensed contractor at developer’s expense.
5. Each new residential dwelling unit shall be metered individually. 
6. For new developments with multiple residential dwelling units; the City has accepted, as an alternative, a public master meter for the development provided there is a private sub-meter for each individual dwelling unit. The Owner or Home Owner’s Association would be responsible for the ownership, maintenance, reading, and replacement of the private sub-meters. There shall be a shared agreement for the shared water supply line and private water and sewer facilities among the owners. This should be addressed in the CC&Rs or maintenance agreement.
7. Provide a separate irrigation water meter for common area landscaping. Meter shall be managed and paid for by the Owner or Homeowner’s Association for the development. The existing irrigation mater located along the property frontage is owned and operated by the City, and shall not be utilized for the development.
8. [bookmark: _GoBack]Per the latest approved California Fire Code, all new residential units shall be equipped with fire sprinkler system. Water services that feed the fire sprinkler system along with the domestic water system shall be equipped with a dual check valve device.
9. Buildings requiring an NFPA 13 or NFPA 13R automatic sprinkler system for fire protection shall have a dedicated fire service connection to a public water main with a double check detector backflow assembly. Location of the backflow assembly must be approved by Fire Department.
10. Private on-site fire hydrants shall be served by a private fire main that is looped on-site with two connections to a public water main. Each connection shall have a double check detector assembly for backflow protection.
11. Hot tap connections will not be allowed for size on size connections, and 6-inch connections to an 8-inch water main. The connection shall be a cut-in tee with three valves for each end of the tee. Provide a connection detail on the improvement plans for all cut-in tee connections.
12. On-site water and sewer mains shall be private, 8” minimum. Design shall be in accordance with latest edition of the City of Oceanside Water, Sewer and Recycled Water Design and Construction Manual. Indicate which mains and lines are private on plans
The following conditions shall be met prior to the approval of engineering design plans.
13. Any water and/or sewer improvements required to develop the proposed property will need to be included in the improvement plans and designed in accordance with the Water, Sewer, and Recycled Water Design and Construction Manual.
14. All public water and/or sewer facilities not located within the public right-of-way shall be provided with easements sized according to the Water, Sewer, and Recycled Water Design and Construction Manual.  Easements shall be constructed for all weather access.
15. No trees, structures or building overhang shall be located within any water or wastewater utility easement.
16. All lots with a finish pad elevation located below the elevation of the next upstream manhole cover of the public sewer shall be protected from backflow of sewage by installing and maintaining an approved type backwater valve, per the latest adopted California Plumbing Code.
17. Per City of Oceanside Ordinance No. 14-OR0565-1, the developer shall pay a recycled water impact fee since the proposed project is not within 75 feet of a recycled water main. The impact fee shall be established by submitting a formal letter requesting the City to determine this fee, which is based on 75% of the design and construction cost to construct a recycled water line fronting the property in Vista Way.
18. If a property goes through a zone change and an increase in density occurs, a water and sewer study will be required to be prepared by the developer at the developer’s expense and reviewed and approved by the Water Utilities Department. The water study shall demonstrate that adequate fire flows and pressures can be delivered to the development. The sewer study shall analyze downstream capacity of the existing sewer collection system. Additional off-site improvements may be required as a result of the studies.
19. Connections to a public sewer main with a 6-inch or larger sewer lateral will require a new sewer manhole for connection to main per Section 3.3 of Water, Sewer, and Recycled Water Design and Construction Manual. 
20. Connection to an existing sewer manhole will require rehabilitation of the manhole per City standards. Rehabilitation may include, but not be limited to, re-channeling of the manhole base, surface preparation and coating the interior of the manhole, and replacing the manhole cone with a 36” opening and double ring manhole frame and lid. 
21. A separate irrigation meter and connection with an approved backflow prevention device is required to serve common landscaped areas and shall be displayed on the plans. 
22. Provide peak irrigation flows per zone or control valve to verify size of irrigation meter and reduced pressure principle backflow device on Landscape Plans. 
23. Provide stationing and offsets for existing and proposed water service connections and sewer laterals on plans.
24. Each dwelling unit shall have a separate sewer lateral connection to the private sewer collection system. 
25. Where private sewer system is shared with other tenants, a Homeowner’s Association or Property Management Company and CC&Rs should address the maintenance, repair, and replacement of “shared” sewer lateral or facilities.
26. Any unused water services or sewer laterals by the proposed development shall be abandoned in accordance with Water Utilities requirements.
The following conditions of approval shall be met prior to building permit issuance.
27. Show location and size of proposed water meter(s), including sub-meters, on site plan of building plans. Show waterline from proposed meter to connection point to each residence.
28. Show location and size of proposed sewer lateral(s) from private sewer main to connection point at each residence.
29. Provide a fixture unit count table and supply demand estimate per the latest adopted California Plumbing Code (Appendix A) to size the water meter(s) and service line(s).
30. Provide drainage fixture unit count per the latest adopted California Plumbing Code to size sewer lateral for the development.
31. Water and Wastewater buy-in fees and the San Diego County Water Authority Fees are to be paid to the City at the time of Building Permit issuance per City Code Section 32B.7.
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