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To be filled out by Project Planner   

Project/property address and/or APN: 3710 Vista Way (APN: 165-493-47)

Project description: Tentative Map, Development Plan, and Density Bonus for proposed 20-unit detached senior housing project on a vacant 2.08 acre site


To be filled out by ARC Division Reviewer   

☒  1st    ☐  2nd    ☐  3rd    ☐  4th   Review	   

Staff member: Tim Rise

Phone number: (760) 435-4101

E-mail: trise@oceansideca.org

☐ Approved w/Conditions
☐ Returned for Corrections – 15 Days
☒ Returned for Corrections – 30 Days
(include attachments/forms on TRAKiT, if applicable): 

[insert/paste comments in Times New Roman, 13 pt font, numbered, 1.5 spacing]

1. All homes will be required to have fire sprinklers per NFPA 13.
2. Water meter size will be determined by the fire sprinkler demand.
3. Fire access roadways shall be a minimum of 28’ with NO parking on either side of the street.
4. Turning radius shall be 30’ inside and 50’ outside.
5. Show driveway widths for emergency access gate.
6. Show emergency gate set back off North Way. The gate shall be set back a minimum of 30’.
7. Knox key switch and Opticom required for gate.
8. Hydrants must be within 400’ of all exterior walls of the structures.
9. Confirm on plans if hydrants will be public or private system.
10.  If hydrants are private a deferred submittal will be required to the Oceanside Fire Department for review. Note: private system must be looped.
11. A fire master plan will be required.
12. Prior to delivery of combustible materials or start of combustible construction, paved vehicle access roads capable of supporting vehicle loading (78,000 lbs) must be installed.  In addition, the approved, permanent water supply (fire hydrants) must be installed, tested and placed in service prior to delivery of combustible materials or start of combustible construction.
13. Addresses shall be 4” in height and visible from the street with contrasting colors.
14. Smoke and carbon monoxide alarms required per 2019 California Fire Code, California Building Code and California Residential Code.
15. Pre-con meeting will also be required prior to combustibles being dropped on site.
16. [bookmark: _GoBack]The City is in the process of implementing a citywide Community Facilities District (CFD) for Public Safety.  The CFD would place an annual per unit fee on projects which meet the criteria for inclusion.  The project you are submitting appears to meet the criteria for inclusion in the proposed Public Safety CFD.  It is expected that your project will be required to annex into the CFD as a condition of approval.
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