City of Oceanside

Fire Department

Fire Prevention Bureau – Plans Examiner

760 435 4101

Fax:  760 435 4084

PLAN REVIEW COMMENTS


Date:


June 29, 2022
Reviewed by:

Tim Rise
Project Name:

Vista Senior Housing
Project Address:
3710 Vista Way
Project:


New Homes
Plan Check Number:
T21-00002
Applicant:

Reza Shera



rezashers@gmail.com
*Resubmit plans to the Oceanside Fire Department with corrected items clouded and delta numbered.  Required changes must be made to all sets resubmitted to the City.    For questions regarding comments, please email OFDplanreview@oceansideca.org or telephone (760) 435-4101. 

Plans must be fully assembled if the set contains more than one sheet.  To check plan review status, please call (760) 435-4101. 

** To speed up the recheck process, please provide a response letter and delta and number applicable changes on the plans. 
*** Note:   AN ADDITIONAL $222 FEE WILL BE CHARGED WHEN PLANS REQUIRE A THIRD SUBMITTAL.

Comments
1. Fire access plan that was approved by Fire Marshal D. Parsons on August 19, 2021 is now unacceptable/void due to the changes in the site plan after this above date. 

2. Please provide an updated fire access plan to the Oceanside Fire Department for review.

3. Fire access plan shall show all hose pull distances from an approved fire access roadway. Hose pulls cannot exceed 200’ of all exterior walls of the structure. This is measured on an approved route around the structures and not as the crow flies.
4. Show hydrant locations on site plans. Hydrants need to be within 600’ of BLDGs 16,17 and 18 if these are determined to be R3. If the building division determines these to be R2 the hydrant distance to all exterior side of the structure will be 400’.
5. If some buildings are determined to be R2, the locations of the FDC will need to be determined. These FDC will need to have a hydrant within 40’ of the FDC.
