PLAN CHECK CORRECTIONS

Date:			January 13, 2017

Plans Reviewed By: 	Ibrahim Hassan

Phone No.:		760-435-5800

Email:			ihassan@iecorporation.com

Alt Review Contact:	Mabel Uyeda

Phone No.:		760-435-5819

Email:			muyeda@ci.oceanside.ca.us

PermitTRAK No.:	BLDG16-3580

Submittal No.:		1 (revised 1/13/17 by M.U.)

Project Name:	EL CORAZON AQUATICS CENTER - CONSTRUCT 15,000 SF BLDG

Project Address:	3306 Senior Center Drive

Project Description:	EL CORAZON AQUATICS CENTER – ENGINEERING CIP, ALL PLAN SET INCLUDES BUILDING, LANDSCAPE, GRADING AND IMPROVEMENT PLANS

STATUS:		RETURN FOR CORRECTIONS

Resubmit plans to Oceanside Development Services for processing and distribution to Water Utilities. To speed up the recheck process, please note on this list (or a response letter to item numbers of this list) where the correction items have been addressed on the plans and return the correction list with your next submittal.

REVIEW COMMENTS:

- Proposing:

  - 3” meter with 3” RPBA (lockers in West Bldg and pool), provide 3” sub-meter on water supply line after meter and optional 2” sub-meter for water supply line to lockers.

  - 2” meter with RPBA (Hall or East Building?, see #3 below)

  - 8” fire service with DCDA

- Sheet UT-01 shall show proposed 12” PVC C900 water main in access road to parking lot off of ‘CC’ street as shown in Water Utilities redline markups dated 10/27/16. If water services will be crossing over proposed 12” PVC water main, the services must have a minimum 3’ of cover. Therefore, the proposed 12” PVC main will need to be lowered so that the services can cross over it with minimum 12” of vertical clearance from bottom of service to top of water main.

- Sheet UT-01 what will the proposed 2” meter serve? Label on plan. The 2” water meter shall have a reduce pressure (RP) per OSD W-12.

- For each water meter provide table showing existing and proposed fixtures, fixture quantity and total fixture unit (FU) count and provide water demand calculations per 2016 California Plumbing Code (CPC) per Chapter 6 or Appendix A. . Be sure to indicate if water closets and urinals are flush valve or tank type. Indicate in table which meter and building or use it would supply.

- Landscape Plans call out an existing 2” irrigation meter on Sheet L-2.02. City records show a 1.5” meter #67121857. Utility Site Plan calls out a 1.5” which is correct. Change meter size to 1.5” on any relevant sheets. Provide calculations to verify the existing 1.5” meter is adequate to handle the existing and proposed irrigation flows. If a large meter is required, then the incremental increase in water buy-in fees would shall be paid including any service connection upsize.

- All trees shall be a minimum 5’ from fire hydrant, meter, service line, or sewer lateral; and 10’ from water and sewer mains.

- Show proposed water and sewer services and mains on landscape plans.

- All irrigation piping shall be purple pipe with meter lids, valve can lids, and appurtenances that meet the recycled water requirements as described in the Water, Sewer, and Reclaimed Water Design and Construction Manual.

- Provide drainage fixture unit counts to confirm size of proposed 6” sewer lateral before connecting to existing sewer manhole in Senior Center Access Drive. For 6” sewer lines, manholes are required at every 300-foot spacing, pipe diameter size transition points, horizontal bends, change in slopes in vertical alignment, and connection point.

- Location of water and sewer connection points from civil plans to building shall be consistent, including pipe diameter sizes.

- A public reclamation water system shall be constructed to serve each lot and/or parcels that are located in the proposed Project in accordance with the City of Oceanside Ordinance No. 91-15.  The proposed reclamation water system shall be located in the public right-of-way and design shown on plans.

- Water and Wastewater Buy-in fees and the San Diego County Water Authority Fees are to be paid to the City at the time of Building Permit issuance per City Code Section 32B.7.