PermitTRAK No.: BLDG18-2639, 40, 41, 42

Plans Reviewed by: Phil Scattergood, CASp

Phone #:  (760) 435-3942

Email: pscattergood@ci.oceanside.ca.us

Structural plan review by: William Teachworth, PE

Phone #:  (760) 435-5117

Email: wteachworth@ci.oceanside.ca.us

Date: 09/06/2018

Job Address: Pending (Del Oro Gateway shell Buildings)

APN:  160-680-33-00

Owner: DEL ORO GATEWAY LLC

Contact:  Roland Lo (213) 537-0910

Date of Application:  08/10/2018

#### Plan Check Corrections

#### City of Oceanside

Building Division

300 N Coast Hwy

Oceanside, CA 92054

(760) 435-3950

Project description:  Del Oro Gateway – four new shell buildings, site lighting, EV charging stations, and retaining walls,

Schools:  Oceanside Unified

- Please note on the first plan sheet that the applicable Code for this project is the 2016 edition of the California Code of Regulations (CCR); Title 24 (California Building Standards Code), which has 12 parts and the typical applicable parts for most non-residential projects are listed below. The submitted plans did not clearly state the applicable code for the project and the code parts reference in Jurisdiction/Permits section on the cover sheet included and outdated non-applicable code of the 2014 CGBSD which was probably intended to reference part 11 of Title 24 the 2016 California Green Building Standards Code or CALGreen and did not include the applicable 2016 California Energy Code.

Part 2: The 2016 California Building Code (CBC)

Part 3: The 2016 California Electrical Code (CEC)

Part 4: The 2016 California Mechanical Code (CMC)

Part 5: The 2016 California Plumbing Code (CPC)

Part 6: The 2016 California Energy Code

Part 9: The 2016 California Fire Code (CFC)

Part 11: The 2016 California Green Building Standards Code (CALGreen)

The 2016 triennial edition of the California Code of Regulations, Title 24 (California Building Standards Code) applies to all occupancies that applied for a building permit on or after January 1, 2017, and remains in effect until the effective date of the 2019 triennial edition. The California Building Standards Commission website at http://www.bsc.ca.gov/codes.aspx has information on where the codes can be viewed online or purchased.

- Plan approval is also required from the City of Oceanside Fire and Water Departments, Engineering and Planning Divisions prior to a permit being issued.

- It is the responsibility of the architect or engineer of record or non-licensed designer if applicable to assure that all requirements of the latest adopted editions of the California Code of Regulations are satisfied and incorporated in the plans, specifications.

- The plan preparer shall sign each sheet they are responsible for and not all of the plan sheets in the submitted plan sets were signed, see CA B&P sections 5536.1 and 6735.

- Note on Title Sheet: “The discharge of pollutants to any storm drainage system is prohibited. No solid waste, petroleum byproducts, soil particulate, construction waste material or wastewater generated on construction site or by construction activities shall be placed, conveyed or discharged into the street, gutter or storm drain system”.

- Provide an accurate complete sheet index, the sheet index on the cover sheet of the submitted plans listed some plan sheets that were not in the plan sets [A0.12, A0.20, M2.0, E1.1, E2.2, E3.1, E3.2, E4.1, & E6.1] and there were also plan sheets in the plan sets that were not listed in the sheet index [A0.33, M0.6, M2.4, E0.0, E8.1, E8.2, E8.3, E8.4, E9.0, E10.0, & E11.0]

- There was only one Building Permit Application that was provided at the time the plans were submitted and before the plans can be approved and permits issued a separate Building Permit Application will be required for each of the four buildings that must also include an actual street number and street name. So far there are four permit numbers assigned as follows: BLDG18-2639 for bldg. #1, BLDG18-2640 for bldg. #2, BLDG18-2641 for bldg. #3, BLDG18-2642 for bldg. #4; please provide a completed permit application with address and description of work for each of the separate buildings.

- Provide a more detailed Scope of Work section on the cover sheet of the plans that lists the items requiring building permits that the plan set is intending to provide details for. CMU and cast in place concrete retaining walls require a building permit and are processed as separate permits from buildings so, please provide a separate Building Permit application for retaining walls as well as plan details (see structural plan comments).

- The City of Oceanside does not approve boiler plate accessibility details unless they meet current 2016 CBC code requirements for accessibility and it is clear that the details are properly cross referenced to the actual site and floor plans and represent proposed conditions. The submitted plans included couple sheets of accessibility details that would be code compliant however they were not crossed referenced to on the actual site plan included in the submitted plan set. A reference to see civil drawings that are not a part of the building permit plan set cannot be approved and accessible path maximum slopes and rises must be listed be provided on the site plan of the building permit plan set.

- The submitted plans did not clearly show actual van accessible parking spaces for either of the standard and EV parking spaces that must have the access aisle on the passenger side of the van accessible parking space, also the parking signage locations were not shown at the lot entry points; detail the TOWED SIGN detail on sheet A0.31 of the submitted plans listed a towing company and phone number that is not local to the City of Oceanside, provide the actual local towing company and phone number that will be used or indicate the information will be provided on the sign prior to approval of the final inspection. Please be aware that the term handicapped as was listed in the submitted site plan key notes is not a term used in the 2016 CBC accessibility requirements or the ADA and is also considered a derogatory term to many persons with disabilities so, it would be more appropriate to use the term accessible.

- Provide a copy of the work order for the new electrical services from the utility provider SDG&E that shows the available fault current will not exceed 42,000 AMPS as was indicated on sheet E6.0 of the submitted plans or note the on the plans that a copy of the work order that matches will be provided to the field inspector or the plans will be revised and recalculated to account for any higher available fault current.

- Submit legible cut sheets for all of the exterior lighting fixtures that shows the lighting fixtures meet the City of Oceanside Lighting ordinance; full cut off, and not more than 4040 lumens.

- Note on the plans the project will provide construction waste management per 2016 CALGreen section 5.408 Construction Waste Reduction, Disposal and Recycling.

Note: The following Structural corrections have been noted from the City of Oceanside Consultant Bill Teachworth PE, (760) 435-5117.

- On Buildings 1, 2, 3 and 4 Foundation Plan, shear wall callout information is too small and unreadable.

Enlarge.

- For all buildings 1, 2, 3 and 4 foundation plan specifies shear walls 2, 4D, 4 or 6.  The shear wall schedule detail 1/S11 specifies A35 or LTP4 shear clips for all shear walls.  At shear transfer details 1A & 3/S510, graphically show the A35 or LTP4 shear clip.

- Foundation plan sheets S210, S220, S230 and S240, the continuous concrete foundation schedule depth of 1’-6” and 2’-0” needs a detail to explain depth.  Is it depth below cold joint per detail1/S500 or the overall depth below top of concrete slab?  Clarify on plans. Also clarify actual depth of the thickened slab edge (footing from top of concrete slab to the cold joint).

- At footing / grade beam details 2 & 3/S500, specify vertical depths of pour strips from top of slab to cold joint.

- At shear transfer detail 3/S510 and 1A/S510, graphically show the shear wall edge nail (EN) into the top plate.

- At detail 1A/S510, graphically show the shear wall symbol on the shear wall.

- For buildings 1, 2, 3 and 4, all the building shear walls are shown on foundation plan and not the roof framing plan.  The top of shear wall shear transfer is detail 1A/ S510 which is shown on roof framing plan.  On roof framing plans, specify shear transfer detail 1A/S510 applies to all proposed shear walls. In-lieu-of this, show all the shear walls on roof framing plan with detail A/S510 above a typical shear wall.

- At detail 2A/S490, specify spacing of Simpson LTTI31 horizontal tie straps.

- The building addition wall height / plate height is 14’.  The American Wood Council National Design Specifications for Wood Construction (NDS) Special Design Provisions For Wood and Seismic (SDPWS) Table 4.3.4 sets a shear wall height to width ration = 2 to 1.  Plan show 14 to 18’ high walls.  Therefore all designed wood shear walls shall be 7to 8 feet wide. The shear wall aspect ratio H/B for seismic forces may be increased up to 3.5 to 1 provided the tabulated unit shears are reduced by the multipliers 2b/h.

- On roof framing plan sheets S221, S230 and S240, clearly identify / show the glue-lam roof beam supporting the high roof shear wall and spanning to the opposite exterior wall.

- On roof framing plans on sheets S221, S230 and S240, clearly identify the glue lam roof beams extending continuously underneath the high roof shear walls. Clearly show / identify the glue lam roof beams span from exterior wall to opposite exterior wall. This means for building 2, the glue lam roof beam will span 55’. In building 3, the glue lam roof beam will span 50’.  Building 4 glue lam roof beam spans 52

- On sheet S230 and S240 (buildings 3 & 4) roof framing plan, (3) HSS headers are called out. Are the (2) HSS headers side by side or stacked below each other.  Clarify on plans. Also are the (2) HSS headers welded together?

- On sheet S230, gridline 1, detail 2/S510 is a detail cut through the (2) HSS headers. However detail 2/S510 does not show the (2) HSS headers.  Detail 2/S510 is roof parapet bracing.

- At the HSS holdown at detail 1/S120, the anchor schedule for HSS holdowns (3) #4 each side @ 3” OC or (2) #4 each side @ 3” OC or (1) #4 each side @ 3” OC. Provide a detail to graphically depict the #4 ties each side at 3” OC.  Each side of what? Each side of anchor bolts?  Do you start spacing the ties directly under the column?

- Page 152 High Roof Framing Design Engineering Calcs, specifies “Pre-Manufactured Roof Trusses.”  Therefore revise South High Roof detail 2/S221 and 3/S230 to specify “Bidder Design Pre-Manufactured Roof Trusses.” South high roof is currently shown as conventional framing.

- Provide a letter from the Geotechnical Engineer for their review and approval of the foundation plan, for geological conformance with the Nova Services Soils Report.

- Add / imprint the City of Oceanside Building Division’s Special Inspection Form PC-20 onto plans.  Complete, sign and date the Special Inspection Form before imprinting onto plans.

- At building 3 roof framing plan sheet S2.30, along grid line 2, specify length of the Simpson CS14 drag strap across pre-fab roof trusses.

- At all buildings 1, 2, 3 and 4, cross reference detail 3/S510 (shear wall, shear transfer parallel to roof trusses) and detail1/S510 to the exterior shear walls occurring parallel to roof framing.

- At typical interrupted top / bottom plate splice, detail 7/S110, detail the ¼” bent plate. It appears to be a steel L shaped angle.  One piece of the L shaped angle leg is removed to fit around HSS pipe.  The detail shall show this.  Also specify length of each L shape angle leg.

- At detail 1A/S510, the pre-fab. Roof trusses may or may not provide the truss hanger models and sizes.  The deferred roof truss calculations sometimes specify “hanger Sizes by others.’  This may be a field issue later.

- At buildings 2, 3 and 4, the high roof shear walls bear perpendicular to the roof trusses. Roof framing plans appear to show 6” X 6’ beams.  Clarify and detail the solid blocking between the roof trusses.  Is the solid blocking the 6” x 6”?  Provide detail to explain framing.

- Submit for plan review, the Nova Services Soils Report Project 2014160 dated June 19, 2017.

I will review this Soils Report in recheck.

- At trash enclosure floor plan sheet A0.33, the trash enclosure has a solid roof. CBC classifies the trash enclosure as a: building.  Provide engineering calcs for the lateral and vertical design of the masonry trash enclosure storage buildings in-accordance with ASCE 7-10.

- Provide roof framing plans and details for the trash enclosure storage building. Show rafter joist sizes and spacing.  Detail weld connection of steel roof deck to steel roof joists.

- Provide trash enclosure masonry construction details. Detail reinforcement in masonry walls.

- Provide foundation plans and details for the trash enclosure storage building. Detail masonry wall anchorage to foundation.

- Detail trash enclosure steel roof deck joist connection to steel header beams. Detail the steel header connections to steel support columns.  Detail bottom of steel column connections to top of masonry walls.  Show all weld connections.

- Specify on trash enclosure building: “masonry walls shall be solid grouted in all cells.”

- Add trash enclosure building areas to Scope of Work.  Also specify their occupancy and type of construction

- Wall sections 1/A6.01, 1 & 2/A6.03, 4/A6.06, 1 & 3/A6.07 and 2/A6.08 show fabric canopies per keynote 11.  Canopy fabric shall have California State Fire Marshall Certificate for the flame resistant fabric. Imprint a full size copy of the State Fire Marshall’s Certificate onto plans. On plans also specify the fabric manufacturer and model type.

- Provide engineering construction plans and calcs for the Building Storefront Glazing Systems or add this item to the Deferred Submittal List.

- Make all changes on the original tracings or CAD file and submit 3 new sets of corrected plans and the previous set that was date stamped with the previous submittal date and labeled with the assigned PermitTRAK permit number and City in red on the outside edge of the cover sheet. If changes do not need to be made on all of the sheets, only the changed sheets may be slip sheeted into old sets and then note the sheets that have been changed in a response letter to this item.  Also submit one set of the sheets that were changed and removed.

- To speed-up the recheck process, please note on this list (or a response letter to item numbers of this list) where the correction items have been addressed on the plans and return the correction list with your next submittal.

- For your information if you do not already have access to a set of the current triennial addition of CCR Title 24 you can view copies of some parts online at http://www.bsc.ca.gov/codes.aspx

Please indicate here if any changes have been made to the plans that are not a result of corrections from this list. If there are other changes, please briefly describe them and where they are located in the plans. Have changes been made to the plans not resulting from this correction list? Please indicate: Yes___ No___