PLAN CHECK CORRECTIONS

Date:			October 13th, 2020

Plans Reviewed By: 	Ibrahim Hassan

Phone No.:		760-435-5857

Email:			Ihassan@oceansideca.org

Alt Review Contact:	Bryan Kallenbaugh

Phone No.:		760-435-5860

Email:			bkallenbaugh@oceansideca.org

PermitTRAK No.:	BLDG20-3418

Submittal No.:		1

Project Address:	217 S COAST HWY

Project Description:	HOOLIHAN VET CLINIC - DEMO (E) NON-BEARING WALLS,

STATUS:	RETURN FOR CORRECTIONS

Resubmit plans to Oceanside Development Services for processing and distribution to Water Utilities. To speed up the resubmittal process, please note on this list (or a response letter to item numbers of this list) where the correction items have been addressed on the plans and return the correction list with your next submittal.

REVIEW COMMENTS:

- City records show the building is occupied by two units/suites. Will this become one unit?

- Indicate the location of the existing water 5/8” water meter on site plan. If there are no grading or improvement plans show where the service connects to the main.

- 34 Fixture units per plans. Calculations indicate the existing 5/8” commercial water meter is inadequate based on the AWWA operating capacity of the meter (provided in the Water Utilities Fee Table), and must be upsized to a ¾” commercial water meter minimum. Indicate the new meter size on the plans and pay buy in fees.

  - The existing 5/8” meter will be used as a $19,512 credit toward the $26,277 3/4” water meter (fee schedule below).

- Indicate size and location of the existing/proposed sewer lateral. If there are no grading or improvement plans show where the sewer lateral connects to the sewer main.

- Water and Wastewater Buy-in fees and the San Diego County Water Authority Fees are to be paid to the City at the time of Building Permit issuance per City Code Section 32B.7