Water Utilities Project Comments & Conditions

Date:	August 28th, 2019

Planner:	Tiffany Chen

From: 	Bryan Kallenbaugh

RE:	2027 Mission Avenue – UEI College - Submittal #2

ACUP19-00003, BLDG19-3023

STATUS: REVISE AND RESUBMIT

The following comment(s) will need to be addressed to deem the application complete.

- Show existing water main on east side of building along with the existing water meter for the building and existing fire service lines and valves.

- Show existing utility poles and guy wires.

- Install new DCDA backflow assembly on the fire service line. DCDA shall be equipped with an FDC. Show location on plans. DCDA should be located within 40’ of a fire hydrant, and on the same side of the driveway as the fire hydrant.

- Per Fire Department comments, remove existing FDC and PIV. Call out on the site plan.

- Provide description of work to be performed in auto area, medical classroom, dental classroom, and pharmacy tech lab. Depending on type of work to be performed the sewer drainage system may require a sand & oil interceptor, inspection manhole, and/or an amalgam separator.

- Provide list of chemicals to be used in medical classroom, dental classroom, and pharmacy tech lab.

The tentative map/development/project shall reflect all requested comments above in next resubmittal for review and approval by the Water Utilities Department prior to the Planning Commission’s consideration.

General conditions:

- The developer will be responsible for developing all water and sewer utilities necessary to develop the property. Any relocation of water and/or sewer utilities is the responsibility of the developer and shall be done by an approved licensed contractor at the developer’s expense.

- All Water and Wastewater construction shall conform to the most recent edition of the Water, Sewer, and Recycled Water Design and Construction Manual or as approved by the Water Utilities Director.

- The property owner shall maintain private water and wastewater utilities located on private property.

- Water services and sewer laterals constructed in existing right-of-way locations are to be constructed by an approved and licensed contractor at developer’s expense.

- Each new commercial suite shall be metered individually.

- Buildings requiring an NFPA 13 or NFPA 13R automatic sprinkler system for fire protection shall have a dedicated fire service connection to a public water main with a double check detector backflow assembly. Location of the backflow assembly must be approved by Fire Department.

The following conditions shall be met prior to the approval of engineering design plans.

- All public water and/or sewer facilities not located within the public right-of-way shall be provided with easements sized according to the Water, Sewer, and Recycled Water Design and Construction Manual.  Easements shall be constructed for all weather access.

- Any water and/or sewer improvements required to develop the proposed property will need to be included in the improvement plans and designed in accordance with the Water, Sewer, and Recycled Water Design and Construction Manual.

- No trees, structures or building overhang shall be located within any water or wastewater utility easement.

- An inspection manhole as described by the Water, Sewer, and Recycled Water Design and Construction Manual, shall be on each building sewer lateral and the location shall be called out on the approved engineering plans.

- An Oil and Sand Interceptor, as described by the latest adopted California Plumbing Code Chapter 10, relating to garages, gasoline stations, wash racks or when deemed necessary shall be shown on building plans at each building sewer in an appropriate location and shall be maintained in accordance with the Fats, Oil, and Grease permit. The location shall be shown on the approved Engineering Plans with reference to Building Plans for design and detail.

- Connections to public sewer main with 6-inch or larger sewer lateral will require a new sewer manhole for connection to main per Section 3.3 of Water, Sewer, and Recycled Water Design and Construction Manual.

- Provide stationing and offsets for existing and proposed water service connections and sewer laterals on plans.

- Any unused water services or sewer laterals by the proposed development or redevelopment, shall be abandoned in accordance with Water Utilities requirements.

The following conditions of approval shall be met prior to building permit issuance.

- Show location and size of existing and proposed water meter(s) on site plan of building plans. Show waterline from proposed meter to connection point to building or residence.

- Show location and size of existing and proposed sewer lateral(s) from property line or connection to sewer main to connection point at building or residence.

- Provide table of fixture count and flow calculations per the latest adopted California Plumbing Code to size water meter and service lines on site plan of building plans.

- Provide drainage fixture unit count per the latest adopted California Plumbing Code to size sewer lateral for property.

- If a Sand and Oil Separator is required, then building plans must show drainage fixture unit count and calculations per the latest California Plumbing Code to size oil and sand separator and show on plans the location, make and model of separator, inlet/outlet piping, and a plumbing schematic of the separator along with the required appurtenances at each building sewer lateral.

- Water and Wastewater Buy-in fees and the San Diego County Water Authority Fees are to be paid to the City at the time of Building Permit issuance per City Code Section 32B.7.