Oceanside Fire Requirements

Community Development Department

Planning Division

TO:	Project Planning

FROM:	Anne Marie Bland

Plans Examiner

DATE:	September 10, 2014

SUBJECT:	GPA 13-00002

Mission Avenue @ Academy Road

420 New Dwelling Units

*Applicant must submit revised plans to the Fire Department

The tentative map/development/project shall reflect all requested changes and those changes shall be resubmitted for review and approval by the Fire Department prior to the Planning Commission’s consideration.

The following items will need to be addressed in order to deem the application complete.

- Provide a full-sized scaled site plan showing fire access roadway widths, proposed fire hydrant locations and building heights.  Fire access roadways must comply with the following:

  - Apparatus access roads shall have a minimum unobstructed width of 28 feet.  A minimum vertical clearance of 14 feet shall be provided for the apparatus access roads.

  - Buildings or portions of buildings more than thirty-five (35) feet in height shall be provided with a street, driveway, or designated fire lane not less than 35 feet wide which shall be able to accommodate fire department aerial apparatus and designed in a matter so that ladder truck operations can be affected on at least one side of the building which has openings into its interior.  Such street, alley, driveway, or designated fire lane shall be located not more than 15 feet (15’) from buildings at a point adjacent to the highest building or portion thereof.

  - The fire department access roadway shall be provided with adequate turning radius for fire department apparatus: a 50 foot outside and 30 foot inside turning radius.

  - Fire access roadways greater than 150 ft in length must be provided with approved cul-de-sac.

  - Parking not permitted on fire access roadways 28 ft in width.  Parking on one side permitted on roadways up to 32 ft and parking permitted on both sides of the roadway on roadways greater than 32 ft.

  - Access roadway grade may not exceed 12%.

- All dwellings must be fire sprinklered.

- Blue hydrant identification markers shall be placed as per Oceanside’s Engineers Design and Processing Manual Standard Drawing No. M-13.