Water Utilities Project Comments & Conditions

Date:	March 8, 2016

To:	Richard Greenbauer

From: 	Mabel Uyeda, Assistant Engineer

RE:	Melrose Heights Proposed Residential and Mixed-use PDP – Submittal #4

GPA13-00003, ZA13-00004, T13-00006, D13-00011, ZA154-00001,

CUP15-00003

STATUS: REVISE AND RESUBMIT

The following comments (s) will need to be addressed to deem the application complete

- Sewer Service Analysis for the Melrose + Oceanside Project in the City of Oceanside dated January 14, 2016 has been reviewed. Sewer study will need to address review comments.

- Water Service Analysis for the Melrose + Oceanside Project in City of Oceanside dated January 13, 2016 is still pending completion of review. The City’s hydraulic water model is not consistent with results of the study. Once the review is completed, the study may need to be revised and resubmitted.

- All water and sewer in public roadways including Sports Park Way shall be public.

- Since the on-site sewer system will be private, the proposed easement shown between Lots PA2-P1 (Lot 7) and PA2-P3 (Lot 6) on Sheet 5 of TM is no longer required. The sewer lateral and on-site manholes before connecting to City’s sewer manhole in Melrose Drive shall be private.

The tentative map/development/project shall reflect all requested changes and those changes shall be resubmitted for review and approval by the Water Utilities Department prior to the Planning Commission’s consideration.

General Conditions

- The developer will be responsible for developing all water and sewer utilities necessary to develop the property. Any relocation of water and/or sewer utilities is the responsibility of the developer and shall be done by an approved licensed contractor at the developer’s expense.

- All Water and Wastewater construction shall conform to the most recent edition of the Water, Sewer, and Reclaimed Water Design and Construction Manual or as approved by the Water Utilities Director.

- The property owner shall maintain private water and wastewater utilities located on private property.

- Water services and sewer laterals constructed in existing right-of-way locations are to be constructed by an approved and licensed contractor at developer’s expense.

- All Water and Wastewater construction shall conform to the most recent edition of the Water, Sewer, and Reclaimed Water Design and Construction Manual or as approved by the Water Utilities Director.

- Per the 2010 California Fire Code, all new residential units shall be fire sprinklered.

- Each commercial unit shall be individually metered with a reduced pressure principle backflow assembly.

The following conditions shall be met prior to the approval of engineering design plans.

- All public water and/or sewer facilities not located within the public right-of-way shall be provided with easements sized according to the Water, Sewer, and Reclaimed Water Design and Construction Manual.  Easements shall be constructed for all weather access.

- Any water and/or sewer improvements required to develop the proposed property will need to be included in the improvement plans and designed in accordance with the Water, Sewer, and Reclaimed Water Design and Construction Manual.

- No trees, structures or building overhang shall be located within any water or wastewater utility easement.

- All lots with a finish pad elevation located below the elevation of the next upstream manhole cover of the public sewer shall be protected from backflow of sewage by installing and maintaining an approved type backwater valve, per the latest approved California Plumbing Code.

- The developer shall construct a public reclamation water system that will serve each lot and or parcels that are located in the proposed project in accordance with the City of Oceanside Ordinance No. 91-15.  The proposed recycled water system shall be located in the public right-of-way or in a public utility easement.

- Connections to public sewer main with 6-inch or larger sewer lateral will require a new sewer manhole for connection to main per Section 3.3 of Water, Sewer, and Reclaimed Water Design and Construction Manual.

- Provide stationing and offsets for existing and proposed water service connections and sewer laterals on plans.

- Provide documentation in CC&Rs and maintenance agreement indicating the maintenance, repair and ownership of on-site sewer will be private and indicate responsible party. Provide documentation on how the on-site sewer system will be maintained.

- On-site water system in private streets will be public and within a minimum 20-ft wide public water easement.

- On-site sewer shall be private because of several dead-end drives and difficult. Sewer lateral and pipe connection to public main shall be considered private. Private sewer system shall be designed in accordance with the latest Water, Sewer, and Reclaimed Water Design and Construction Manual.

- Each residential units shall be metered individually. For multi-unit residential buildings where frontage space of individual meters per residential unit is limited, Water Utilities has allowed master metering with private sub-meters for each residential unit.

- On-site water shall be public and within 20-foot wide easement. Access for maintenance vehicles must meet Fire Department requirements and roadway must be designed to handle vehicle loads.

- Show location and size of dedicated fire service connection for each building with double check detector assembly.

- Show location and size of dedicated irrigation water service and meter with reduced pressure principle backflow assembly dedicated for residential landscaped areas.

- Show location and size of dedicated irrigation water service and meter with reduced pressure principle backflow assembly dedicated for commercial landscaped areas; unless both residential and commercial areas are owned and maintained by same entity or property owner.

- For all commercial and industrial uses, an Inspection Manhole, described by the latest Water, Sewer, and Reclaimed Water Design and Construction Manual, shall be installed in each building sewer lateral and the location shall be called out on the approved Improvement Plans.

- Each commercial unit shall be individually metered with a reduced pressure principle backflow assembly.

- A Grease Interceptor, as required per City of Oceanside Ordinance 07-OR0021-1 relating to food service establishments shall be shown on sewer lateral when deemed necessary in an appropriate outside location and shall be maintained by the property owner. The grease interceptor shall be shown on engineering plans with reference to building plans for design and detail. Grease interceptors shall not be shared with other commercial units.

- Show on improvement plans the any proposed off-site water or sewer improvements required for the development of the Project.

- The City has received the sewer study for this development, Sewer Service Analysis for the Melrose Heights Project in the City of Oceanside dated January 14, 2016. Based on the sewer study, the existing 8” sewer main in Melrose Drive must be replaced with a 10” gravity sewer from Willowbrook Drive south to the Melrose Heights development. The proposed improvements shall be included in the engineering plans and constructed as part of this development. Minor comments made to the sewer study will need to be addressed prior to approval of this entitlement application.

- The Tentative Map Development Plan did not show the proposed water easement for public water system within private streets on-site. The Final Map must show the water easement and limits prior to final approval of engineering plans.

- The on-site sewer is private. Final Map and engineering plans should not show any proposed on-site sewer easements in private streets.

- Connections to public water mains shall be cut in with tee and 3 isolation valves at each end unless noted otherwise by Water Utilities Department.

The following conditions of approval shall be met prior to building permit issuance.

- Show location and size of proposed sewer laterals to new residential dwelling units or residential buildings and commercial units.

- Show location and size of proposed water meters to each residential and commercial unit. Multiple dwelling units with limited frontage space for meter locations shall be allowed to have a master meter per building if each residential unit is privately sub-metered. Show size and location of each private sub-meter on building plans.

- Show service line and meter size and location on building plans.

- If a Grease Interceptor is required per City of Oceanside Ordinance 07-OR0021-1, then building plans must show sizing calculations per the latest California Plumbing Code, the location, the make and model, and plumbing schematic showing the required appurtenances at each building sewer lateral.  Provide sizing calculations on building plans.

- Provide table of fixture count and flow calculations per the latest California Plumbing Code to size master water meter and service lines on building plans. This shall be confirmed with proposed water service connections shown on improvement plans. Provide fixture count calculations to verify size of private sub-meters, if used.

- Water and Wastewater Buy-in fees and the San Diego County Water Authority Fees are to be paid to the City and collected by the Water Utilities Department at the time of Building Permit issuance.

- All Water Utilities Fees are due at the time of building permit issuance per City Code Section 32B.7.