Water Utilities Project Comments & Conditions

Date:	March 23, 2018

To:	Richard Greenbauer

From: 	Mabel Uyeda, Senior Civil Engineer

RE:	Melrose Heights Proposed Residential & Mixed-use PDP – Submittal #7

GPA13-00003, ZA13-00004, T13-00006, D13-00011, ZA154-00001,

CUP15-00003

STATUS: APPROVED WITH THE FOLLOWING CONDITIONS

General Conditions

- For developments requiring new water service or increased water service to a property, the landowner must enter into an agreement with the City providing for landowner’s assignment of any rights to divert or extract local groundwater supplies for the benefit of the property to receive new or increased water service, in return for water service from the City, upon such terms as may be provided by the Water Utilities Director.

- All existing active and non-active groundwater wells must be shown on conceptual, grading, and improvement plans.

- The developer will be responsible for developing all water and sewer utilities necessary to develop the property. Any relocation of water and/or sewer utilities is the responsibility of the developer and shall be done by an approved licensed contractor at the developer’s expense.

- All Water and Wastewater construction shall conform to the most recent edition of the Water, Sewer, and Recycled Water Design and Construction Manual or as approved by the Water Utilities Director.

- The property owner shall maintain private water and wastewater utilities located on private property.

- Water services and sewer laterals constructed in existing right-of-way locations are to be constructed by an approved and licensed contractor at developer’s expense.

- Per the latest adopted California Fire Code, all new residential units shall be fire sprinklered.

- Each commercial unit shall be individually metered.

- Provide a separate irrigation water meter with reduced pressure principle backflow device for common area landscaping. Meter shall be managed and paid for by the Homeowner’s Association or Property Management company/property owner for the residential or commercial development.

The following conditions shall be met prior to the approval of engineering design plans.

- All public water and/or sewer facilities not located within the public right-of-way shall be provided with easements sized according to the Water, Sewer, and Recycled Water Design and Construction Manual.  Easements shall be constructed for all weather access.

- Any water and/or sewer improvements required to develop the proposed property will need to be included in the improvement plans and designed in accordance with the Water, Sewer, and Recycled Water Design and Construction Manual.

- No trees, structures or building overhang shall be located within any water or wastewater utility easement.

- All lots with a finish pad elevation located below the elevation of the next upstream manhole cover of the public sewer shall be protected from backflow of sewage by installing and maintaining an approved type backwater valve, per the latest approved California Plumbing Code.

- The developer shall construct a public recycled water system that will serve each lot and or parcels that are located in the proposed project in accordance with the City of Oceanside Ordinance No. 14-OR0565-1.  The City does not have a planned recycled water system within the vicinity of the project. Therefore, the developer shall pay an in-lieu fee by submitting a formal letter requesting the City to determine this fee that is based on 75% of the design and construction cost to construct a recycled water system that would serve the Project. The fee will be based on the total frontage length of recycled water main that would have been designed and constructed in Melrose Drive (1800 ft) and Oceanside Blvd (2,200 ft), a total length of approximately 4,000 feet.

- Connections to public sewer main with 6-inch or larger sewer lateral will require a new sewer manhole for connection to main per Section 3.3 of Water, Sewer, and Recycled Water Design and Construction Manual.

- Provide stationing and offsets for existing and proposed water service connections and sewer laterals on plans.

- Provide documentation in CC&Rs and maintenance agreement indicating the maintenance, repair and ownership of on-site sewer will be private and indicate the responsible party. Provide documentation on how the on-site sewer system will be maintained.

- On-site sewer system shall be private. Private sewer mains including the connections to public sewer mains shall be considered private. Sewer laterals from private main to connection point at building shall be shown on precise grading plans. Connection point at building shall be consistent with location and elevation on building plans. Private sewer system shall be designed in accordance with the latest Water, Sewer, and Recycled Water Design and Construction Manual and shown on the precise grading plans. Provide sewer calculations for proposed private on-site sewer mains with the precise grading plan submittal.

- Water and sewer mains shall meet the minimum Department of Public Health separation requirements. Private sewer mains shall be located outside of the public water easement, areas of exception to this will be subject to the Water Utilities Department approval and would require an Encroachment Removal Agreement.

- Improvement plans, precise grading plans, and Final Map should not have public sewer easements for the private on-site sewer in private streets.

- Each residential unit shall be metered individually. For multi-unit residential buildings, a master meter that would serve a pair of buildings is acceptable provided that each residential unit will have a private sub-meter that can be read without entering the premises.

- On-site water shall be public and within a minimum 20-foot wide easement. Access for maintenance vehicles must meet Fire Department requirements and roadway must be designed to handle H-20 loading.

- The Tentative Map Development Plan did not consistently meet the minimum 20-ft wide water easement for public water mains within private streets. The improvement plans, precise grading plans, and Final Map must show the proper easement width prior to final approval of stated documents.

- Show location and size of dedicated fire service connection for each building with double check detector assembly on improvement plans. Location of fire service connections at building shall be consistent with Building and Fire Plans.

- Show location and size of dedicated irrigation water services and meters with reduced pressure principle backflow assembly dedicated for common landscaping within residential areas on improvement plans. Location of irrigation meters and services shall be consistent with Landscape Plans.

- Show location and size of dedicated irrigation water service and meter with reduced pressure principle backflow assembly dedicated for commercial landscaped areas; unless both residential and commercial areas are owned and maintained by the same entity or property owner.

- Each commercial unit shall be individually metered with a reduced pressure principle backflow assembly.

- A Grease Interceptor, as required per City of Oceanside Ordinance 07-OR0021-1 relating to food service establishments shall be shown on sewer lateral when deemed necessary in an appropriate outside location and shall be maintained by the property owner. The grease interceptor shall be shown on the precise grading plans with reference to building plans for design and detail. Grease interceptors shall not be shared with other commercial units. Sewer laterals from food service establishments with grease interceptors are required to have sample boxes. Sample boxes that are a minimum 24-inch size will not be required to have an inspection manhole.

- For all commercial and industrial uses, an Inspection Manhole, described by the latest Water, Sewer, and Recycled Water Design and Construction Manual, shall be installed in each building sewer lateral and the location shall be called out on the approved engineering plans, except where a minimum 24-inch sample box is already required.

- Based on results of the Sewer Service Analysis for the Melrose+Oceanside Project in the City of Oceanside revised August 31, 2017, off-site sewer improvements will be required to be constructed as part of this Project. They include upsizing the existing 8” gravity sewer in Melrose Drive from Meadowbrook Drive to Willowbrook Drive (just south of N. Sante Fe Ave) with a 10-inch PVC sewer main. The preliminary alignment provided as part of the entitlement application must be revised when submitting improvement plans. The proposed sewer alignment shall be centered within the slow travel lane. It shall not straddle the striping of travel lanes nor be located within the bike lane.

- At no point in the public sewer upsize in Melrose Drive shall the new sewer main be less than 10-inch in diameter, regardless of the slope.

- The existing 8-inch sewer in Melrose Drive shall be abandoned-in-place by filling main and capping any open ends in accordance with Water Utilities requirements. All existing manholes along the abandoned sewer shall be removed and properly disposed.

- Private sewer laterals 6” or larger will require a manhole at connection to private sewer main.

- The Water Service Analysis for the Melrose+Oceanside Project in the City of Oceanside dated August 30, 2017 was reviewed by Water Utilities. There are no off-site improvements required for the Project. However, the on-site water loop within commercial Planning Area 1 located west of Melrose Drive shall be designed with a 10-inch loop and 10-inch connections to existing 12-inch water main in Oceanside Blvd. Planning Areas 2 and 3 will have an 8-inch looped system because of its multi-family residential land use. Figure 3 of the study identifies a 10-inch loop for the commercial Planning Area 1. On page 15, paragraph 2 of the study incorrectly states that all three planning areas will have an 8-inch loop. Improvement plans shall reflect a 10-inch looped system within the Planning Area 1.

- Connections to public water mains shall be cut in with a tee and 3 isolation valves at each end, unless noted otherwise by Water Utilities Department.

- All dead-end public water mains 150 feet or less shall have a fire hydrant at end of line and water services connections as close to the end as possible. Any dead-end water mains over 150 feet shall be looped.

- Any unused water services or sewer laterals shall be abandoned in accordance with Water Utilities requirements.

- Foot print of any proposed grease interceptors for commercial property shall be shown on the precise grading plans including water supply lines from meter to building and sewer lines from property line to building connection points.

- Improvement plans must provide adequate clearances and access, including a paved access road, to any proposed or existing public sewer manholes that is impacted by the development.

- Provide sewer calculations with precise grading plans to confirm the design is in compliance with the latest Water, Sewer, and Recycled Water Design and Construction Manual.

The following conditions of approval shall be met prior to building permit issuance.

- Show location and size of proposed sewer laterals to new residential dwelling units or residential buildings and commercial units.

- Provide drainage fixture count information in building plans to confirm each building sewer lateral size and slope.

- Provide table of fixture count and flow calculations per the latest adopted California Plumbing Code to size water meters including sizing of private sub-meters (if used) on building plans. This shall be verified with the proposed water service connections shown on improvement plans.

- Show water supply lines from each City water meter to the proposed connection point of each residential or commercial building. If metering per unit, show supply line from water meter to each unit.

- Where master City water meters are approved by the Water Utilities Department for a multi-unit building, there must be private sub-meters proposed for each residential or commercial unit. Private water meters shall be located such that they can be read and maintained without entering the premises.

- If a Grease Interceptor is required per City of Oceanside Ordinance 07-OR0021-1, then building plans must show sizing calculations per the latest adopted California Plumbing Code, the location, the make and model, and plumbing schematic of the required appurtenances at each building sewer lateral.

- Water and Wastewater Buy-in fees and the San Diego County Water Authority Fees are to be paid to the City at the time of Building Permit issuance per City Code Section 32B.7.