Water Utilities Project Comments & Conditions

Date:	March 7, 2017

Planner:	Scott Nightingale

From: 	Mabel Uyeda

RE:	522 N. Tremont Row Homes - Submittal #1

RZA17-00001, RD17-00001, RRP17-00001

STATUS: APPROVED WITH THE FOLLOWING CONDITIONS

General Conditions:

- The developer will be responsible for developing all water and sewer utilities necessary to develop the property. Any relocation of water and/or sewer utilities is the responsibility of the developer and shall be done by an approved licensed contractor at the developer’s expense.

- All Water and Wastewater construction shall conform to the most recent edition of the Water, Sewer, and Reclaimed Water Design and Construction Manual or as approved by the Water Utilities Department.

- The property owner shall maintain private water and wastewater utilities located on private property.

- Water services and sewer laterals constructed in existing right-of-way locations are to be constructed by an approved and licensed contractor at developer’s expense.

- Each new residential dwelling unit shall be metered individually.

- Fire sprinkler and irrigation services may be supplied from the domestic meter to each residential unit.

- Provide a separate sewer lateral connection to public sewer main for each parcel.

- Storm water shall not enter City’s sanitary sewer system. If Roof Terrace has sink, it must not allow storm water from entering drain.

The following conditions shall be met prior to the approval of engineering design plans.

- Any water and/or sewer improvements in public right-of-way or easement that is required to develop the proposed property will need to be included in the improvement plans and designed in accordance with the Water, Sewer, and Reclaimed Water Design and Construction Manual.

- No trees, structures or building overhang shall be located within any water or wastewater utility easement.

- All lots with a finish pad elevation located below the elevation of the next upstream manhole cover of the public sewer shall be protected from backflow of sewage by installing and maintaining an approved type backwater valve, per the latest adopted California Plumbing Code.

- Provide stationing and offsets for existing and proposed water service connections and sewer laterals on plans.

- Any existing sewer laterals to parcels that will not be used shall be shown on plans to be abandoned at public sewer main per Water Utilities Inspector.

- Show location and size of existing 5/8” water meter with ¾” water service off of existing 8” PVC water main in Alley, as well as, any proposed water service line and meter size(s) on plans. If not used, then show water service to be abandoned on plans.

The following conditions of approval shall be met prior to building permit issuance.

- Show location and size of existing 5/8” water meter, as well as, any proposed meter size(s) on site plan of building plans.

- Show location and size of existing and proposed sewer laterals to proposed dwelling units.

- Provide table of fixture count and flow calculations per the latest adopted California Plumbing Code to size water meter(s) and service line(s) in building plans.

- If a larger water meter is required, then the incremental increase in water and sewer buy-in fees from the existing meter to proposed meter size will be charged.

- Water and Wastewater Buy-in fees and the San Diego County Water Authority Fees are to be paid to the City at the time of Building Permit issuance per City Code Section 32B.7.