Oceanside Fire Requirements

Community Development Department

Planning Division

TO:	Project Planning

FROM:	Anne Marie Bland

Plans Examiner

DATE:	April 11, 2018

SUBJECT:	T18-00002

301-307 West Street

Proposed three story, VB, R-2, eight units

Fire Department Conditions of Approval

- Proposed three story, Type VB construction, eight unit R-2 occupancy must be fire sprinklered per NFPA 13.

- Fire sprinkler system water flow switch and control valves must be monitored by a UL listed monitoring station.

- Fire sprinkler system fire department connection (FDC) must be located at the corner of West and Cleveland Streets.  FDC must be located within 40 feet of a public fire hydrant.  Fire hydrant located on the northwest corner of Cleveland and West Streets is acceptable.

- Landscaping may not obstruct fire department connection or fire sprinkler control valves on the DCDA.

- Required rescue windows must be accessible to fire department ladders.  Show horizontal and vertical accessibility to rescue windows on the permit plan submittal.