Water Utilities Project Comments & Conditions

Date:	March 1, 2018

Planner:	Mary Wright

From: 	Mabel Uyeda

RE:	West Homes 301-307 West St, New 8 New 3-story, attached Residential Condo Units on Condemned Commercial Building - Submittal #1

T18-00002, D18-00003, V18-00001, RC18-00002

STATUS: APPROVED WITH THE FOLLOWING CONDITIONS

General conditions:

- For developments requiring new water service or increased water service to a property, the landowner must enter into an agreement with the City providing for landowner’s assignment of any rights to divert or extract local groundwater supplies for the benefit of the property to receive new or increased water service, in return for water service from the City, upon such terms as may be provided by the Water Utilities Director.

- All existing active and non-active groundwater wells must be shown on conceptual, grading, and improvement plans.

- The developer will be responsible for developing all water and sewer utilities necessary to develop the property. Any relocation of water and/or sewer utilities is the responsibility of the developer and shall be done by an approved licensed contractor at the developer’s expense.

- All Water and Wastewater construction shall conform to the most recent edition of the Water, Sewer, and Recycled Water Design and Construction Manual or as approved by the Water Utilities Director.

- The property owner shall maintain private water and wastewater utilities located on private property.

- Water services and sewer laterals constructed in existing right-of-way locations are to be constructed by an approved and licensed contractor at developer’s expense.

- Each new residential dwelling unit shall be metered individually.

- Provide a separate irrigation water meter with reduced pressure principle backflow device for common area landscaping. Meter shall be managed and paid for by the Homeowner’s Association for the development.

- Per the latest approved California Fire Code, all new residential units shall be equipped with fire sprinkler system.

The following conditions shall be met prior to the approval of engineering design plans.

- All public water and/or sewer facilities not located within the public right-of-way shall be provided with easements sized according to the Water, Sewer, and Recycled Water Design and Construction Manual.  Easements shall be constructed for all weather access.

- Any water and/or sewer improvements required to develop the proposed property will need to be included in the improvement plans and designed in accordance with the Water, Sewer, and Recycled Water Design and Construction Manual.

- No trees, structures or building overhang shall be located within any water or wastewater utility easement.

- All lots with a finish pad elevation located below the elevation of the next upstream manhole cover of the public sewer shall be protected from backflow of sewage by installing and maintaining an approved type backwater valve, per the latest adopted California Plumbing Code.

- The developer shall construct a public recycled water system that will serve each lot and or parcels that are located in the proposed project in accordance with the City of Oceanside Ordinance No. 14-OR0565-1.  The proposed recycled water system shall be located in the public right-of-way or in a public utility easement. If the development is more than 75 feet from an existing or planned recycled waterline, then the developer shall pay an in-lieu fee. The developer shall submit a formal letter requesting the City to determine this fee that is based on 75% of the design and construction cost to construct a recycled water line fronting the property on Cleveland Street.

- An inspection manhole as described by the Water, Sewer, and Recycled Water Design and Construction Manual shall be on the sewer lateral at property line and the location shall be shown on the approved engineering plans.

- Connections to public sewer main with 6-inch or larger sewer lateral will require a new sewer manhole for connection to main per Section 3.3 of Water, Sewer, and Recycled Water Design and Construction Manual.

- The sewer connection to manhole in Site Plan, Sheet A1.1 of entitlement plan submittal shows the lateral connection against the direction of flow in the existing 8” VCP sewer in Cleveland Street. Final improvement plans shall show sewer lateral at right angle to manhole, or remove and relocate existing manhole.

- A separate irrigation meter and approved backflow prevention device is required to serve common landscaped areas and shall be displayed on the plans.

- Provide stationing and offsets for existing and proposed water service connections and sewer laterals on plans.

- Any proposed fire hydrant runs over 150 feet in length shall become public mains (minimum 8-inches) and shall have meters placed off these public mains to help facilitate the continuous flow of water on these proposed dead-end runs.

- Where private sewer system is shared with other tenants or owners, a Homeowner’s Association or Property Management Company and CC&Rs should address the maintenance, repair, and replacement of “shared” sewer lateral or facilities.

- Any unused water services or sewer laterals by the proposed development or redevelopment, shall be abandoned in accordance with Water Utilities requirements.

The following conditions of approval shall be met prior to building permit issuance.

- Show location and size of existing and proposed water meter(s) on site plan of building plans. Show waterline from proposed meter to connection point to building or residence.

- Show location and size of existing and proposed sewer lateral(s) from property line or connection to sewer main to connection point at building or residence.

- Point of water and sewer connections at building in building plans shall be consistent with that shown on precise grading plans.

- Provide table of fixture count and flow calculations per the latest adopted California Plumbing Code to size water meter and service lines on site plan of building plans. Provide similar calculations for typical residential unit to size private water-submeters.

- Show private water sub-meters for each residential unit. Private meters shall be located such that they can be read and maintained without entering the unit.

- Water and Wastewater Buy-in fees and the San Diego County Water Authority Fees are to be paid to the City at the time of Building Permit issuance per City Code Section 32B.7.